| FIELD SERVICE REPORT TEMPLATE |  |  |  |
| --- | --- | --- | --- |
| THURSDAY 13TH NOVEMBER 2025 |  |  |  |
| Summary |  |  |  |
| The unit experienced a critical system failure due to a suction line refrigerant leak and subsequent compressor burnout. New compressor and filter dryer installed, system evacuated and charged with R404A. Unit is operational and pulling temperatures successfully. Follow-up inspection required in 7 days to confirm pressure stability. |  |  |  |
| Job and Customer Information |  |  |  |
| Q# QUESTION |  | RESPONSE |  |
| 1. Job or work order number |  | #E234653 |  |
| 2. Company name (service provider) |  | Demo Company |  |
| 3. Client or site name |  | Rutherford |  |
| 4. Service location address |  | Basement Prep Kitchen, North End |  |
| 5. Client contact (phone / email) |  | jbluth@rutherforddemosite.com |  |
| 6. Technician name and ID |  | J. Hunt |  |
| 7. Date of visit |  | 11 Nov 25 |  |
| 8. Time of arrival |  | 11 Nov 25 01:20 PM |  |
| 9. Time of departure |  | 11 Nov 25 02:05 PM |  |
| 10. Type of service (installation / maintenance / repair / inspection / other) |  | Maintenance and repair |  |
| 11. Initial problem or work request |  | The tenant reported that the freezer compartment of the unit is over freezing, resulting in a significant ice buildup on the back panel and floor of the freezer. This excessive icing is restricting access to food and preventing the proper seating of the freezer drawer/door. Cooling performance in the refrigerator section is simultaneously reported as inadequate (temperatures above the set point). |  |
| Equipment and Environmental Details |  |  |  |
| Q# QUESTION |  | RESPONSE |  |
| 12. Equipment make and model |  | Make: Frigidaire Pro-Line; Model: FPLR- 4500-SS (Side-by-Side Commercial Unit) |  |
| 13. Serial number |  | 987632103 |  |
| 14. Equipment location or tag ID (if any) |  | Basement Prep Kitchen, North End; Tag ID: COMM-REF-B2 |  |
| 15. Description of problem or defect found |  | Found a suction line leak at the filter dryer weld joint. The compressor is dead, drawing high LRA and tripping thermal overload due to low charge and a dirty condenser. |  |
| Page 1 of 4 | Ref:8311983 : 13,November 2025 14:34:13 IST |  | Powered By: |

|  | FIELD SERVICE REPORT TEMPLATE |  |  |  |
| --- | --- | --- | --- | --- |
| 16. Photo evidence of defects or damages (attach or upload) |  |  |  |  |
| 13 Nov 25 02:27 PM |  |  |  |  |
| 17. Environment type (indoor / outdoor / hazardous / confined space / other) |  | Confined Space (Narrow service corridor behind unit) |  |  |
| 18. Cleanliness of unit |  | Poor. Heavy dust/lint buildup observed on the condenser coil and fan blades upon inspection of the back panel. This contributed to poor heat exchange. |  |  |
| 19. Ambient conditions (temperature, controlled or not) |  | Temperature: 28 degrees (Uncontrolled/Warm); Humidity: Approximately 65% (High humidity environment due to proximity to wash area) |  |  |
| 20. Issues encountered during service |  | Major delay due to the required 4-hour vacuum pump time to clear contamination. Access in the tight corridor was difficult, plus a 2-hour delay to collect a non-stock compressor. |  |  |
| Technical Measurements (If Applicable) |  |  |  |  |
| Q# QUESTION |  | RESPONSE |  |  |
| 21. Nameplate values (input V / A, output V / A, rating) |  | Input V: 208V AC (3-Phase); Input A: 12.5A; Rating: 3.2kW (based on compressor/fan nameplates). |  |  |
| 22. Measured readings (single phase or three phase) |  | Supply: 210V AC, 3-Phase. Readings: L1-L2: 209V; L2-L3: 211V; L3-L1: 210V. Measured Amps (Post-repair): L1: 4.1A; L2: 4.0A; L3: 4.2A (within spec). |  |  |
| 23. Battery details (quantity, voltage, current, strings) |  | N/A |  |  |
| 24. Battery operation verified |  | N/A |  |  |
| 25. Maintenance bypass switch operation verified |  | N/A |  |  |
| 26. Load circuits tested and ready for power up |  | YES |  |  |
| Work Performed and Resources Used |  |  |  |  |

| Q# QUESTION |  | RESPONSE |  |
| --- | --- | --- | --- |
| 27. Description of work performed or actions taken |  | Isolated unit and manually defrosted coils. Recovered refrigerant. Cut out and brazed in a new compressor and filter dryer. Pressure tested with nitrogen, then evacuated the system for 4 hours due to contamination. Recharged with 2.8 kg of R404A. Tested unit operation and verified temperature pull-down. |  |
| 28. Parts or materials used (name, model / part number, quantity) |  | Embraco Compressor (P/N: E-78-459-B), Sporlan Filter Dryer (P/N: A-22-108), 2.8kg R404A refrigerant, and 4 sections of 15% Silver Brazing Rod. |  |
| 29. Safety procedures followed |  | YES |  |
| 30. PPE worn |  | YES |  |
| 31. Follow-up actions or additional requirements |  | Recommend replacement of the condenser fan motor. Observed bearing noise and slight vibration during the final test. Motor is functioning now but shows signs of imminent failure, likely due to prolonged high-ambient operation. Advised the Building Manager. |  |
| 32. Service or customer follow-up needed (details) |  | Scheduled follow-up needed in 7 days. Call to confirm the unit is holding temperature and maintaining optimal pressures after the major component replacement. Customer advised to monitor temperatures closely and report any fluctuation immediately. |  |
| Completion and Sign-off |  |  |  |
| Q# QUESTION |  | RESPONSE |  |
| 33. Job status (completed / pending / follow-up required / awaiting parts) |  | YES |  |
| 34. Unit operational Unit is running and pulling down temperature successfully. Freezer reached -15 degrees and Fridge reached 4 degrees within the test period. |  | YES |  |
| 35. Next service date (if applicable) |  | 11 Nov 26 |  |
| 36. Technician notes or observations |  | Observed minor bearing noise from the condenser fan motor. Recommended replacement to prevent future overheating/failure. Customer verbally approved the temporary fix and agreed to the follow-up check next week. All panels secured; workspace cleaned. |  |
| 37. Photo evidence of completed work (attach “after” photos) |  | YES |  |
| Page 3 of 4 | Ref:8311983 : 13,November 2025 14:34:13 IST |  | Powered By: |